## ASHP Checklist
NYS Clean Heat Statewide Heat Pump Program
Standards and Quality Assurance
Air Source Heat Pump Checklist
Updated: 7/1/21
# | Category | Objective / Task Description | Criteria | Document Required / Verification Method | Responsible Party | Program Phase | Defect Category | Reference
C1 | Equipment | Verify installed equipment is as proposed on application, quantity, make and model | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Design Professional / Participating Contractor | Construction | Major
C2 | (Intentionally Blank)
C3 | Installation | Observe condensate line where accessible for leaks. Confirm condensate lines terminate in either a domestic drain or external location. External locations must not terminate onto another heat pump unit or onto a walking surface that could cause slips if condensate freezes. Confirm with the homeowner that there is no indication of condensate line leakage. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Design Professional / Participating Contractor | Construction | Major
C4 | Installation | Verify that safe access to the site and associated equipment has been provided | Situational Awareness | Site Observation | Participating Contractor | Construction | Critical
C5 | Installation | Verify site conditions are consistent with Load Sizing Analysis or a revised energy analysis has been completed. Review of ACCA (Manual J, S, and D) or other approved heating and cooling calculation methodologies, with observed site conditions | Visual Observation / Document Review | Site Observation / NYC ECC EN2/TR8 forms or equivalent | Design Professional / Participating Contractor | Construction | Major | NYC DOB EN2: As Built Energy Analysis
C6 | (Intentionally Blank)
C7
C8 | Installation | Sample for refrigerant leaks at exposed field connections | Functional Test | Refrigerant detector | Participating Contractor | Construction | Critical
C9 | Installation | Verify that exposed new or retrofitted ductwork is properly sealed and insulated if located outside the building's thermal envelope. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | NYC 1RCNY 5000- 01
C10 | Installation | Verify all accessible refrigerant line (indoor and outdoor) set is insulated. Verify that all outdoor refrigerant line set is protected from UV. To comply, no more than 12" of any accessible refrigerant line may be left un-insulated/protected from UV at the outdoor unit connection. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | NYC 1RCNY 5000- 01
C10B | Installation | Verify no more than 1" of any refrigerant line is unprotected at the outdoor unit connection. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Minor
C11 | Installation | Verify the presence of equipment air filters if applicable | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Minor
C12 | Installation | Verify all exposed equipment and pipe supports appear to be properly secured | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C13 | Installation | Verify outdoor unit is installed with sufficient clearances. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C14 | Installation | Verify that the top and bottom clearance of ASHP Terminal Units meet the manufacturer's installation requirements, are sufficient for proper function, and that service panels are clearly accessible. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C14B | Installation | Verify that the side clearances of ASHP Terminal Units meet the manufacturer's installation requirements. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Minor
C15 | Installation | Observe that the outdoor unit is away from or protected from increased sources of water/ice/snow from above (i.e. more than normal precipitation, e.g. beneath drip edge, beneath snow-slide, beneath another heat pump, etc.). The presence of gutters does not provide sufficient protection. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C15B | Installation | Verify that units are above snow depth level according to ACCA Weather Station data as provided by the NYS Clean Heat program | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C16 | Installation | Verify outdoor unit is installed level. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
C16B | Installation | If unit is connected to the building's framing (e.g. wall mounted, or on a connected deck), vibration dampeners are installed. |  |  |  |  | Minor
C17 | Installation | Observe functional testing of equipment in either cooling or heating mode as conducted by contractor or operator, if conditions allow. | Functional Test | Site Observation | Participating Contractor | Construction | Major | C. McCracken / CLEAResult, 2016
C18 | Installation | Verify that electrical disconnect is installed in an accessible location for service. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major | 2020 NFPA 70 / NEC 2020
O1 | (Intentionally Blank)
O2 | Operation | Verify Manufacturer's Warranty has been provided to owner | Document Review | Manufacturers Warranty | Participating Contractor | Occupancy | Req't.
O3 | Operation | Confirm customer/ operator has been provided with training on operation of system. | Document Review | Site Observation / Customer Confirmation | Participating Contractor | Occupancy | Major
O4 | Installation | Confirm that the system owners manual and maintenance instructions are available on site. | Document Review | Approved construction documents | Participating Contractor | Design | Req't.
O5 | Installation | Confirm customer/operator has been provided instructions on controls integration of supplemental heat sources to provide primacy of the ASHP equipment. | Document Review | Site Observation / NYC ECC EN2/TR8 forms or equivalent | Participating Contractor | Construction | Major | NYC 1RCNY 5000- 01